## Instructions
Renewable Energy Data Assessment Checklist
Introduction
This tool is intended to help electricity sector decision makers and analysts evaluate which types of analysis and modeling can be supported with available renewable energy (RE) data and other geospatial data. The tool provides a framework for comparing available RE data to the "best-in-class" and "minimum threshold" data requirements for conducting RE Generator Performance Modeling, Assessments of Technical and Economic RE Potential, Capacity Expansion Modeling, Production Cost Modeling, and Power Flow Modeling. The results are intended to help identify potential data gaps for different RE technologies and analyses and inform future investments in geospatial data. For more information on the full suite of data requirements to support decision-making, see From Data to Renewable Energy Decisions: An Introductory Guide.
Instructions
1) View tabs corresponding to different technologies (e.g., "Wind - Onshore", "Solar PV"). 2) Choose the type of analysis that you wish to undertake for your chosen technology. Descriptions of the analysis are provided for your reference. 3) Enter information about data that is currently available in the "Your Data" column of the data checklist. 4) Enter additional information about the data source, collection methods, vintage, storage location, file size or other details in the "Notes" column of the data checklist. 5) Compare your data to the best-in-class and minimum threshold data requirements. Note: You can print the data checklists by selecting File -> Print
Input Definitions
Data Type
Different types of data are needed to characterize different RE resources. Broadly, RE data falls into two categories: -Resource data characterizes the underlying "fuel" (in the case of solar and wind, solar irradiance and wind speed) needed to produce electricity. These data can be used to predict energy generation. See Technology-Specific Considerations (below) for further information about resource data. -Actual generator performance is measured energy generation from RE power plants.
Temporal Range
The temporal range of a data series is the total period that is observed in the data. -One year: temporal range that includes observations for one 365-day period, with constant intervals between observations (e.g., 5-minute, hourly, daily, monthly) -Multiple years: temporal range that includes observations for multiple sequential or non-sequential 365-day periods, with constant intervals between observations (e.g., 5-minute, hourly, daily, or monthly) -Typical meteorological year (TMY): data series holds hourly or subhourly resource and meteorological values that typify conditions at a specific location over a longer period, such as 30 years. TMY data sets are not averages; they are created by force-sampling values from the multi-year data set for each period (e.g., in a daily TMY data set, January 1 may be sampled from 2003, while January 2 may be sampled from 2009). TMY is the preferred data type for Technical Potential Analysis because it represents typical patterns, such as seasonality, over a long period, and helps smooth the impacts of unusual conditions such as drought or El Nino. Multiple years of data can also be used in place of TMY if it is not available. On the other hand, Production Cost Modeling usually requires one real year of data (rather than a TMY data set) that is time-synchronous with load data to capture the effects of underlying weather patterns that drive both solar and wind resource and electricity demand.
Temporal Resolution
Renewable energy resources vary temporally; depending on the resource, the energy generation potential changes throughout the day, month, year, and from year to year. Capturing this temporal variability is crucial for many types of analysis. Hourly or subhourly temporal resolution for wind and solar data is preferred for all types of analysis in order to represent natural variations in the resource. However, existing models can make use of monthly or even annual average resource data.
Spatial Resolution
Renewable energy resources also vary spatially. The degree of change across a specified distance can depend on many factors. Therefore, the spatial resolution can have a significant effect on the applicability of a data set. Spatial resolution for renewable resource data varies from very fine (e.g., 1-km by 1-km grid cells) to coarse (40-km by 40-km grid cells). For Technical Potential, Capacity Expansion, and Production Cost Modeling, high spatial resolution will be important for modeling across the region under study, whereas point specific data can be useful for Generator Modeling at the location. Wind resource modeling is more effective at higher spatial resolutions (e.g., 2-km by 2-km grid cells) because the resource is highly dependent on terrain. A coarser resolution is typically sufficient for modeling solar resources.
Technology-Specific Considerations
Wind
Wind data may be measured, or modeled, or compiled of both measured and modeled data. Spatially, wind data are often presented on a continuous grid (e.g., a wind map of a country of region). In other cases, wind data comprise ground measurements or actual turbine output at particular sites (i.e., discrete sites). Temporally, wind data may range from one-minute data to annual averages. Wind resource data can include wind speed, wind direction, and other parameters at a particular hub height, which refers to the elevation of the hub of a wind turbine from the ground. In some locations, hub height is a significant driver of the wind resource and the type of technology that may be most appropriate. Wind resources at the same site can be very different if measured at 30 meters, 60 meters, or 100 meters off the ground. Decision makers can be misled if they rely on 30-meter wind data to evaluate 100-meter wind development. In the past—15 to 20 years ago—wind turbines typically had hub heights between 30 and 60 meters. Today, utility-scale wind turbine hub heights are typically between 80 and 120 meters. Wind turbines with hub-heights under 30 meters are most commonly deployed for distributed generation applications rather than for utility scale wind farms.
Solar
Solar data may be measured, or modeled, or compiled of both measured and modeled data. Spatially, solar data are often presented on a continuous grid (e.g., a solar map of a country of region). In other cases, solar data comprise ground measurements or actual solar power plant output at particular sites (i.e., discrete sites). Temporally, solar data may range from one-minute data to annual averages. Solar data typically comprise direct normal (DNI), diffuse horizontal (DHI), and global horizontal (GHI) irradiance, or a subset of these three types of solar data. GHI can be calculated by if DNI and DHI are known. -Direct normal irradiance (DNI): solar radiation that comes directly from the sun, wherever it may be in the sky. This radiation hits Earth directly but at different angles throughout the day. Concentrating solar power (CSP) plants depend on this type of resource. -Diffuse horizontal irradiance (DHI): solar radiation that has been scattered and hits Earth’s surface diffusely from many directions. Solar photovoltaic (PV) and other flat-plate collectors can use this type of resource, as well as DNI. -Global horizontal irradiance (GHI): solar radiation that hits a flat surface at any time during the day. It is made up of both DNI and diffuse radiation.

## Wind - Onshore
Onshore Wind Data
Use this sheet to track currently available wind data and assess data needs for the following types of analysis. Scroll down or use the links below for different analysis types.
Jump to:
High-Level RE Data Exploration and Visualization
Mapping and visualization can play a role in early stages of analysis through data exploration as well as later stages through visualization of analytical outcomes.
RE Generator Performance Modeling
Generator modeling refers to performance modeling that estimates the amount of energy that could be produced (generally on an annual basis) by an RE system given the resource potential and system configuration (e.g., wind turbine or solar PV panel type). Beyond its utility for prospecting, generator modeling plays a fundamental role in the other types of analysis presented in this tool, as it provides the means of converting resource potential into energy generation.
Technical and Economic Potential Analysis/Supply Curve Modeling
Renewable energy technical potential represents the achievable energy capacity and generation of a particular technology given resource potential, technology characteristics, topographic limitations, and environmental and land-use constraints. Technical potential analyses provide an upper bound of RE deployment within a region or country, it and serves as a fundamental input into many subsequent analyses, including supply curve modeling, economic potential, capacity expansion, and production cost modeling. Economic potential analysis defines the subset of technical potential that can be developed cost-effectively. The renewable energy resource data requirements for assessing technical and economic potential are the same.
Capacity Expansion Modeling
Capacity expansion modeling is used to analyze long-term electricity system capacity expansion scenarios for power generation technologies. Capacity expansion modeling integrates hourly profiles developed through generator performance modeling to produce scenarios for electricity expansion. These scenarios can inform operational and infrastructure decisions for the power sector. Capacity expansion modeling can also feed into production cost modeling to further resolve generation and transmission requirements and verify and provide additional details on operational decisions. Note: Capacity expansion models require a significant amount of data that is not covered in this checklist. This checklist focuses only on geospatial aspects of the analysis.
Production Cost Modeling
Production cost models optimize electricity scheduling and dispatch over a specified period. These analyses consider costs and constraints related to power generation systems and operations and the physical environment. Production cost modeling provides a robust analytical tool to consider the impacts of variable RE on operational costs of a power system. Production cost modeling can complement capacity expansion modeling to better understand generation and transmission requirements, verify results, and provide details on operational decisions based on capacity expansion model outputs. Note: Production cost models require a significant amount of data that is not covered in this checklist. This checklist focuses only on geospatial aspects of the analysis.
Power Flow Modeling
A power flow model tests the ability of a power system to respond to a real-time disturbance such as an unplanned generator or transmission line outage. Load flow studies model real and reactive power flow, fault tolerance, and contingency response over very short timeframes (seconds to minutes) that correspond to periods of system stress. Evaluation of costs and economics is not typically a component of this type of reliability analysis. Because power flow models focus at very small timescales (usually the few seconds during and following a disturbance, such as a major transmission line or generator outage), these studies rely on the results of operational models such as product costs models to identify periods of potential system stress (e.g., high wind/low load) to study in detail. Note: Production cost models require a significant amount of data that is not covered in this checklist. This checklist focuses only on geospatial aspects of the analysis.
DATA CHECKLIST: High-Level RE Data Exploration and Visualization
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Wind speed | Wind speed
| Wind direction | Wind power density
Air pressure
Air temperature
Temporal Range | At least one of these: | One Year
Multiple years
Typical Meteorological Year (TMY)
Temporal Resolution | Hourly or more frequent | Annual average
Spatial Resolution | 2-km by 2-km spatial resolution or finer | 20-km by 20-km spatial resolution or courser
Geospatial exclusions and constraints | All of these: |  | Check the box if data are available:
Protected areas
Urbanized areas/population density
Natural features
Monuments and parks
Terrain and terrain features
Land-use/land-cover
Infrastructure (roads, transmission)
DATA CHECKLIST: RE Generator Performance Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Wind speed | Wind speed
| Wind direction | Wind power density
Air pressure
Air temperature
Temporal Range | At least one of these: | One Year
Multiple years
Typical Meteorological Year (TMY)
Temporal Resolution | Hourly or more frequent | Monthly average
Spatial Resolution | At least one of these: | 20 km2 spatial resolution or coarser
Discrete site
1-km by 1-km to 5-km by 5-km spatial resolution or finer
System Design Specifications | All of these: |  | Check the box if data are available:
Rated output
Rotor diameter
hub-height
shear coefficient
power curve (with cut-in and cut-out speeds)
DATA CHECKLIST: Technical and Economic Potential Analysis and Supply Curve Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Wind speed | Wind speed
| Wind direction | Wind power density
Air pressure
Air temperature
Temporal Range | At least one of these: | One year
Typical Meteorological Year (TMY)
Multiple years
Temporal Resolution | Hourly or more frequent | Annual average
Spatial Resolution | 1-km by 1-km to 5-km by 5-km spatial resolution or finer | At least one of these:
Discrete site
20-km by 20-km spatial resolution or courser
Geospatial exclusions and constraints | All of these: |  | Check the box if data are available:
Protected areas
Urbanized areas/population density
Natural features
Monuments and parks
Terrain and terrain features
Land-use/land-cover
Infrastructure (roads, transmission)
Additional data needs for Supply Curve Modeling | All of these: |  | Check the box if data are available:
Technical Potential Analysis Results (capacity factor by land parcel)
Electric transmission infrastructure (capacity of individual transmission features)
Substation tie-in cost
Fixed charge rate
Transmission capital cost
Fixed operating cost
DATA CHECKLIST: Capacity Expansion Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Wind speed | Wind speed
| Wind direction | Wind power density
| Air pressure | Capacity factor
Air temperature
Temporal Range | All of these: | At least one of these:
| One year | One year
| Typical Meteorological Year (TMY) | Typical Meteorological Year (TMY)
Temporal Resolution | Hourly or more frequent | Monthly average
Spatial Resolution | 1-km by 1-km to 5-km by 5-km spatial resolution or finer | At least one of these:
20-km by 20-km grid cells or coarser
Discrete sites
DATA CHECKLIST: Production Cost Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Wind speed | Wind speed
| Wind direction | Wind power density
Air pressure
Air temperature
Temporal Range | At least one of these: | One year
Multiple years
One year
Temporal Resolution | At least one of these: | Daily
Subhourly
Hourly
Spatial Resolution | 1-km by 1-km to 5-km by 5-km spatial resolution or finer | At least one of these:
20-km by 20-km spatial resolution or coarser
Discrete sites
DATA CHECKLIST: Power Flow Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Wind speed | Wind speed
| Wind direction | Wind power density
Air pressure
Air temperature
Temporal Range | At least one of these: | At least one of these:
| Multiple years | Typical Meteorological Year (TMY)
| One year | Single period
Temporal Resolution | Subminute | Monthly average
Spatial Resolution | Discrete sites | 20-km by 20-km spatial resolution or coarser

## Solar PV
Solar Photovoltaic Data
Use this sheet to track currently available solar data and assess data needs for the following types of analysis. Scroll down or use the links below for different analysis types.
Jump to:
High-level RE data exploration and visualization
Mapping and visualization can play a role in early stages of analysis through data exploration as well as later stages through visualization of analytical outcomes.
RE Generator Performance Modeling
Generator modeling refers to performance modeling that estimates the amount of energy that could be produced (generally on an annual basis) by an RE system given the resource potential and system configuration (e.g., wind turbine or solar PV panel type). Beyond its utility for prospecting, generator modeling plays a fundamental role in the other types of analysis presented in this tool, as it provides the means of converting resource potential into energy generation.
Technical and Economic Potential Analysis/Supply Curve Modeling
Renewable energy technical potential represents the achievable energy capacity and generation of a particular technology given resource potential, technology characteristics, topographic limitations, and environmental and land-use constraints. Technical potential analyses provide an upper bound of RE deployment within a region or country and serves as a fundamental input into many subsequent analyses, including supply curve modeling, economic potential, capacity expansion, and production cost modeling. Economic potential analysis defines the subset of technical potential that can be developed cost-effectively. The renewable energy resource data requirements for assessing technical and economic potential are the same.
Capacity Expansion Modeling
Capacity expansion modeling is used to analyze long-term electricity system capacity expansion scenarios for power generation technologies. Capacity expansion modeling integrates hourly profiles developed through generator performance modeling to produce scenarios for electricity expansion. These scenarios can inform operational and infrastructure decisions for the power sector. Capacity expansion modeling can also feed into production cost modeling to further resolve generation and transmission requirements and verify and provide details on operational decisions. Note: Capacity expansion models require a significant amount of data that is not covered in this checklist. This checklist focuses only on geospatial aspects of the analysis.
Production Cost Modeling
Production cost models optimize electricity scheduling and dispatch over a specified period. These analyses consider costs and constraints related to power generation systems and operations and the physical environment. Production cost modeling provides a robust analytical tool to consider the impacts of variable RE on operational costs of a power system. Production cost modeling can complement capacity expansion modeling to better understand generation and transmission requirements, verify results, and provide details on operational decisions based on capacity expansion model outputs. Note: Production cost models require a significant amount of data that is not covered in this checklist. This checklist focuses only on geospatial aspects of the analysis.
Power Flow Modeling
A power flow model tests the ability of a power system to respond to a real-time disturbance such as an unplanned generator or transmission line outage. Load flow studies model real and reactive power flow, fault tolerance, and contingency response over very short timeframes (seconds to minutes) that correspond to periods of system stress. Evaluation of costs and economics is not typically a component of this type of reliability analysis. Because power flow models focus at very small timescales (usually the few seconds during and following a disturbance, such as a major transmission line or generator outage), these studies rely on the results of operational models such as product costs models to identify periods of potential system stress (e.g., high wind/low load) to study in detail. Note: Production cost models require a significant amount of data that is not covered in this checklist. This checklist focuses only on geospatial aspects of the analysis.
DATA CHECKLIST: High-level RE data exploration and visualization
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Direct normal irradiance | Diffuse horizontal irradiance
| Diffuse horizontal irradiance | Global horizontal irradiance
Air temperature
Wind speed
Temporal Range | At least one of these: | One Year
Multiple years
Typical Meteorological Year (TMY)
Temporal Resolution | Hourly or more frequent | Annual average
Spatial Resolution | 5-km by 5-km spatial resolution or finer | 20-km by 20-km spatial resolution or courser
Geospatial exclusions and constraints | All of these: |  | Check the box if data are available:
Protected areas
Urbanized areas/population density
Natural features
Monuments and parks
Terrain and terrain features
Land-use/land-cover
Infrastructure (roads, transmission)
DATA CHECKLIST: RE Generator Performance Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Direct normal irradiance | Diffuse horizontal irradiance
| Diffuse horizontal irradiance | Global horizontal irradiance
Air temperature
Wind speed
Temporal Range | At least one of these: | One Year
Multiple years
Typical Meteorological Year (TMY)
Temporal Resolution | Hourly or more frequent | Monthly average
Spatial Resolution | At least one of these: | 20-km by 20-km spatial resolution or courser
Discrete site
5-km by 5-km spatial resolution or finer
System Design Specifications | All of these: |  | Check the box if data are available:
Type (fixed or tracking)
Tilt
Azimuth
DC/AC ratio
System losses
Inverter efficiency
DATA CHECKLIST: Technical and Economic Potential Analysis and Supply Curve Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Direct normal irradiance | Diffuse horizontal irradiance
| Diffuse horizontal irradiance | Global horizontal irradiance
Air temperature
Wind speed
Temporal Range | At least one of these: | One year
Typical Meteorological Year (TMY)
Multiple years
Temporal Resolution | Hourly or more frequent | Annual average
Spatial Resolution | 5-km by 5-km spatial resolution or finer | At least one of these:
Discrete site
20-km by 20-km spatial resolution or courser
Geospatial exclusions and constraints | All of these: |  | Check the box if data are available:
Protected areas
Urbanized areas/population density
Natural features
Monuments and parks
Terrain and terrain features
Land-use/land-cover
Infrastructure (roads, transmission)
Additional data needs for Supply Curve Modeling | All of these: |  | Check the box if data are available:
Technical Potential Analysis Results (capacity factor by land parcel)
Electric transmission infrastructure (capacity of individual transmission features)
Substation tie-in cost
Fixed charge rate
Transmission capital cost
Fixed operating cost
DATA CHECKLIST: Capacity Expansion Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Direct normal irradiance | Diffuse horizontal irradiance
| Diffuse horizontal irradiance | Global horizontal irradiance
Air temperature
Wind speed
Temporal Range | All of these: | At least one of these:
| One year | One year
| Typical Meteorological Year (TMY) | Typical Meteorological Year (TMY)
Temporal Resolution | Hourly or more frequent | Monthly average
Spatial Resolution | 5-km by 5-km spatial resolution or finer | At least one of these:
20-km by 20-km spatial resolution or courser
Discrete sites
DATA CHECKLIST: Production Cost Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Direct normal irradiance | Diffuse horizontal irradiance
| Diffuse horizontal irradiance | Global horizontal irradiance
Air temperature
Temporal Range | At least one of these: | One year
Multiple years
One year
Temporal Resolution | At least one of these: | Daily
Subhourly
Hourly
Spatial Resolution | 5-km by 10-km spatial resolution or finer | At least one of these:
20-km by 20-km spatial resolution or courser
Discrete sites
DATA CHECKLIST: Power Flow Modeling
| Best-in-Class | Minimum Threshold | Your Data | Notes
Data type | All of these: | At least one of these:
| Direct normal irradiance | Diffuse horizontal irradiance
| Diffuse horizontal irradiance | Global horizontal irradiance
Air temperature
Temporal Range | At least one of these: | At least one of these:
| Multiple years | Typical Meteorological Year (TMY)
| One year | Single period
Temporal Resolution | Subminute | Monthly average
Spatial Resolution | Discrete sites | 20-km by 20-km spatial resolution or courser